The City of Pendleton, herein referred to as City, has two wells, Well 11 and Well 11B, that are approximately 50’ apart located near the Wastewater Treatment Resource Recovery Facility, 4300 SW Houtama Road, Pendleton, Oregon.  The wellhouses will be addressed to 4315 SW Houtama Road.  Well 11 has a 10-inch casing for 20-feet and an open bore measured with a diameter of 9-plus-inches+ to a depth of 350-feet.  Well 11B has a 20-inch diameter casing to 257-feet, then a 19-inch open bore to 400-feet.  Static levels are the same on both wells, but the specific capacity is different at both locations.

From ground surface elevation of 1005-feet MSL

- Static water level @ + 218-feet

- Well 11 pump set at 320-feet

- Well 11 specific capacity: + 50 gpm / foot drawdown

- Well 11B pump set at 340-feet

- Well 11B specific capacity: +/- 10 gpm / foot drawdown

- System discharge pressure at 138 psi (319.5’).

The pumping equipment installation is to be coordinated wellhouses construction for both cased wells that includes the necessary piping / fittings to put them into service to a new 16-inch domestic water line.  The wellhouses work will include, but is not limited to, erosion control, site work, rock excavation, rough grading, fine grading, gravel surfacing, building construction, piping, thrust restraint, valves, flow meters, vaults, disinfection systems, fire extinguishers, auxiliary sensors and probes, louvers, exhausts, heating, AC units, some demolition, electrical, and service equipment.  This work has been bid and awarded.

City is purchasing the pumping systems consisting of two each 150 HP motors, discharge heads, column piping, pumping bowls, and access tubes.  Sheet M-101, M-103, M-106, M-201, M-202, and M-205; Well 11 well log, Well 11 caliper log, and Well 11B well log; and Technical Specification 43 05 15 – Owner Furnished Equipment are included in the Request for Proposals packet for pumping systems quotes.  City will provide discharge head submittal for Wellhouses Contractor review and possible field adjustment(s) to pump pedestal(s) prior to pumping systems installation.  Contractor will need to account for access installation of the pumping systems after the pump pedestals (M-106 / M-205) have been completed, with minimum 7-days concrete cure, and before CMU wall construction commences.

City of Pendleton is also purchasing Allen Bradley variable frequency drives (VFDs) for delivery to the project site and installation by Wellhouses Contractor.  City will provide the VFD submittal information to contractor and oversee the testing of the VFDs for start-up of the facilities.

Project is funded from Business Oregon Special Public Works Fund.  After presentation of the application for payment to Owner with Engineer’s recommendation, the amount recommended will become due upon Owner’s deposit receipt of Special Public Works Funds, typically fourteen (14) but up to twenty-eight (28) calendar days, or thirty-five (35) calendar days, whichever comes first.

PROPOSALS ARE TO BE PRESENTED AS A LUMP SUM TOTAL WITH THE FOLLOWING ITEMIZED COST BREAKDOWN:

- Motor

- Discharge head & sole plate

- Two access tubes each

- Column

- Shaft, spiders, and bushings

- Pump with pump curve(s) information included

- Installation / start-up

For more information, contact Jeff Brown at 541 966-0241 or 541.969.3083.

Proposer may provide optional Proposals / Quotes, based on Proposers recommended pump bowl(s) and/or motor(s) as alternatives for Owner approval.  Intent of Proposer must be clear and easy to determine by Owner.  Owner reserves the right to select the best Proposal / Quote solely at the Owner’s discretion.